## PAG Oil
გაზის ტურბინის საპოხი ზეთის შესყიდვა თანმდევი მომსახურებით
# | Description დასახელება | Specifications& Manufacturer Details მახასიათებლები | UOM განზ | QTY რაოდ | Remarks შენიშვნა | ერთ.ფასი დღგ-ს ჩათვლით | ჯამური ღირებულება დღგ-ს ჩათვლით | მოწოდების ვადა
1 | Group V polyalkylene glycol (PAG) based turbine fluid for Gas Turbines | Group V polyalkylene glycol (PAG) based turbine fluid for Gas Turbines Specific gravity(ASTM D4052): Report Appearance/ Colour(ASTM D1500): 2.0 (Max.) Pour point (ASTM D97): -40°C to -42°C Kinematic Viscosity(ASTM D445) at 40°C: 23-26 (centistokes) Total Acid Number (ASTM D974): 0.20 mg KOH/g(max.) Rust Test, Proc. A (ASTM D665): PASS Flash point COC (ASTM D93): 230°C to 232°C Copper corrosion (ASTM D130): 1B (max.) Foam (ASTM D892): 25/0 ml (max.); 0/0 ml (max.); 0/0 ml (max.) Oxidation Characteristics 212 °F/ 100°C Viscosity Change @121 °C,13 days(ASTM D2893B): 3.0% (max.) Oxidation Stability by Rotating Pressure Vessel (minutes)(ASTM D2272): 500 (min.) Oxidation Stability by Rotating Pressure Vessel (modified)(ASTM D2272): 85% (min.) of time in unmodified test Air Release (ASTM D3427): 1.0(max.) Viscosity Index (VI) (ASTM D2270): 125(min.) Thermal Conductivity,40C,watts/m °K (PLTL-73): 0.1 (min.) And lube oil specifications must comply with the GE Energy Standard latest version • GE Energy GEK 32568 | Ltrs | 40000
2 | Solvents or Oil Additives for Lube Oil Cleaning/ Flushing | Solvents or Oil Additives for Lube Oil Chemical Cleaning/ Flushing For Existing Lube Oil Capacity: 40000 ltrs Existing Lube Oil manuafcturer and model: Q8 Volta EP 32 These solvents or oil additives are used for cleaning or flushing of Bearings, hydraulics, gear reducers, Heat exchangers, Oil reservoier, all lube oil piping circuit, and other moving components. | Ltrs | - | The supplier must select the appropriate solvents or oil additives and determine the quantity required.
3 | Existing Lube Oil Chemical cleaning/ flushing and filling the new lube oil | Chemical cleaning/ Flushing and filling the new lube oil 1. Filling the cleaning solvents or oil additives 2. Displacement flushing to the oil reservoir and all lube oil piping circuit. 3. Testing and ensuring the Elimination of deposits and impurities. 4. Draining flushed old oil, 5. Manually mopping out the tank with cleaning agents and cloths. 6. Filling the tank with the new charge of oil by using filatration machine ASTM D6439 Standard Should be followed | lumpsum Units | 2 | The cleaning process/ procedure shall be submitted by the supplier
Note:
1. Listed Turbine oil and solvents Data sheets& Test certificates Should be provided by manufacturer/supplier